Pump Operation Costs as a Function of Operating Flow in Wastewater Treatment

Case Study

Dr. Lev Nelik, P.E., APICS

Pumping Machinery, LLC

Introduction

A centrifugal pump operates at the intersection of its head-capacity (H-Q) curve, and a system curve. The shape of a system curve is determined by hydraulic losses in a system (bends, restrictions, valves partial opening/closing, pipe-length-to-diameter-ratio), as well as the elevation difference between discharge fluid level and suction supply fluid level:

Thus, as system restrictions change (valves open or close, pipes getting plugged-up, and so on), the system curve reflect these changes, forcing the pump to operate at the intersection of the same pump curve and a changed system curve.

It is desirable, of course, for a pump to operate most efficiently, i.e. at a Best Efficiency Point (BEP), because it takes the least amount of energy there.

Also, operating at BEP makes a pump operate more reliably, because this is where internal loads, noise and vibrations are the lowest, as shown at the illustration below:

In fluid transfer application, pipe friction is usually a predominant component of a system curve. Chemical plants are a good example of many such applications, from the hydraulics viewpoint. In waste water treatment applications, particularly lift station, the other extreme is often prominent – i.e. mainly static head (lift) hydraulics, where friction losses are relatively small, in relation to the static lift, as the incoming influent is “lifted” by the effluent pumps to the level of the main waste water treatment facility. In such applications, the main change in a system curve is caused by a change in a wet well level that leads to the pump(s) inlet, and the higher the well level, the lower is a total static head.

Case in Point

A municipality in a Mid-West has been experiencing problems with its influent pumps installed at the end of the wastewater collection tunnel, located almost 350 feet below the surface. These (2) 6,000 HP single stage, double-suction pumps were plagued with reliability issues, such as impeller damage, wear rings failures, noise and vibrations.

Each pump typically operates between 400 to 600 RPM, and lifts up to 60,000 gpm (40,000 gpm is at BEP) from the bottom of the tunnel, to the surface, some 350 feet up, as shown on a simplified conceptual sketch below.

System head is mostly static, with friction head being almost negligible, as shown on a system curve below, which also denotes area of operation of a single pump, as well as two pumps operating in parallel mode. Curves are shown at various level of the influent wet well. Most of the time, the level is such that a pump head is in the range of 350 feet.

At 60,000 gpm (and 600 RPM) a pump requires approximately 35 feet of NPSHR (net positive suction head, required), which must be less then available (NPSHA), with some margin (5 feet margin is typically considered good). Disregarding some minor losses at the short run of the inlet piping and vapor pressure of water at ambient conditions, NPSHA is essentially equal to the water level above the suction centerline plus the atmospheric head (34 feet). Observing the sketch schematic, there appears to be an interesting relationship between a pump head and the suction level:

H = 372 – hS = 338 – NPSHA

Thus, liquid level at the pump inlet determines the pump head. An interesting observation can now be made, regarding the narrowed boundaries within which a pump can operate due such “linked” Head and NPSHA: at low well levels, a concern would be of not to run out of the adequate NPSHA, while at high well level, the pump head could become so low that its performance curve (H-Q) would force it to operate way to the right of the BEP, “running out” into the region where pump would be experiencing high loads, instabilities, and – ironically enough – even not having sufficient NPSHA (at such very high flow rate), despite the fact that the inlet well level is extremely high (but the required NPSHR can still be higher, as it tends to “stonewall” at very high flow, deep past the BEP region).

Energy Costs

a) Operating off-BEP

As discussed above, the pump is restricted to operation within a relatively narrow range of flows, centered around the BEP point. This restriction is due to NPSH considerations, as discussed earlier, but also due to efficiency reasons. At BEP, these 2000 hp pumps have 90% efficiency, but it drops quickly to the left, and to the right, of the best efficiency point. For example, at half flow, pump efficiency drops to 70%, and it shows similar loss of efficiency to the right of the BEP as well.

What does it cost to operate a pump like this per year? At 600 RPM, at BEP (40,000 gpm), each pump consumes power as calculated from the basic formula:

BHP = Q x H x SG / (3960 x eff) = 40,000 x 350 x 1.0 (3960 x 0.90) = 3928 hp, which is 2930 KW

If we assume a 24/360 operation, at $0.07 per KWxHR, the operating cost per year is:

2930 x 24 x 360 x 0.07 = $ 1,772,064

If efficiency is reduced from 90% to 70% (20% difference), we can estimate, approximately, the wasted (“inefficient”) power, as:

2930 x 20/90 = 651 hp (wasted), or, in, similarly, in dollars: 1,772,064 x 20/90 = $ 393,792 ! – per year, per pump.

b) Operating at worn or enlarged clearances

Originally, these pumps were specified to have 0.035” diametric clearance between the impeller and casing wear rings. Unfortunately, stainless rings, also supplied by the manufacturer originally, did not leave much forgiveness to the heavy impeller weight, deflecting the shaft and resulting in rings contact. Once in contact, stainless rings galled, and sometimes seized, resulting in frequent repairs. To combat this, the users kept gradually opening the ring clearances, reaching eventually 0.100” diametral value. This helped keeping the rings from contact, but resulted in additional  (“hidden”) losses – leakage from the high pressure side at the impeller, to a lower pressure side, across the ring clearance. The increased flow leakage reached, as calculated, 3500 gpm above the normal value, which is equivalent to another $140,000 energy waste, per year, per pump.

Once this was recognized, the plant has started to revue options to change the rings materials, to allow operation at the original design clearances. One option being considered is composites, similar to what is routinely used by the US Navy. Using composites, ring clearances can not only be reduced back to the original spec, but likely to even smaller value. As a more extended retrofit, a complete impeller, made from then composite material, is considered as well. This would reduce the rotor weight by nearly 80%, reducing deflections, and thus minimizing a possibility of any contact between the rings, altogether. This, however, is subject of another paper.

Dr. Nelik has 25 years experience with pumps and pumping equipment. He is a Registered Professional Engineer, who has published over fifty documents on pumps and related equipment worldwide, including a "Pumps" section for the Encyclopedia of Chemical Technology (John Wiley), a section for the Handbook of Fluids Dynamics (CRC Press), and a book "Centrifugal and Rotary Pumps: Fundamentals with Applications", by the CRC Press. He is a President of Pumping Machinery, LLC company, specializing in pump consulting, training, and equipment troubleshooting. His experience in engineering, manufacturing, sales, field and management includes: Ingersoll-Rand (Engineering), Goulds Pumps (Technology)., Roper Pump (Vice President of Engineering, and Repair/Overhaul) and Liquiflo Equipment (South-East Regional Sales Manager, and later a President). He teaches pump training courses in the US and worldwide, and consults on pumps operations, engineering aspects of centrifugal and positive displacement pumps, maintenance methods to improve reliability, reduce energy savings, and optimize pump-to-system operation.

Dr. Nelik is an Advisory Committee Member for the Texas A&M International Pump Users Symposium, Editorial Advisory Board Member of Pumps & Systems magazine, and a former Associate Technical Editor of the Journal of Fluids Engineering. He is a Full Member of the ASME, and a Certified APICS. He is a graduate of Lehigh University with Ph.D. in Mechanical Engineering and a Masters in Manufacturing Systems.

Send you comments to: DrPump@Pump-Magazine.com

Back to PUMP MAGAZINE Page

ARTICLES LIST